# SPECIFICATIONS FOR SURVEYING, AERIAL PHOTOGRAPHY AND MAPPING

# OF A PROPOSED TRANSMISSION LINE CORRIDOR FOR USE IN PLS-CADD

# INTRODUCTION

The purpose of this specification is to provide guidance to Engineers in developing a specification for survey data deliverables in such a manner that it integrates seamlessly with PLS-CADD.  The specification provides information for Traditional Ground Survey as well as Aerial LiDAR and could be applied to other surveying methods.  This specification is provided as an example for use in collecting data for PLS-CADD projects and should be reviewed by the project engineer to make sure it meets all current project requirements.  A final specification should be compiled by the project engineer.

# REQUIREMENTS

The survey contractor shall collect and provide survey data such that an accurate digital terrain model of the corridor can be generated.  The method of acquisition shall be determined by the engineer as described in section 3.3 of this specification.  All survey information gathered shall be classified according to the feature code table referenced in this specification.

At a minimum, the survey contractor shall have a staff with competent technical knowledge of current industry standards and processing software, including PLS-CADD.

Poorly or minimally coded PLS-CADD survey models will not be accepted.

Relative accuracy of the point data shall be 0.35’ +/- in both the horizontal and vertical planes at the 95% confidence level.

Absolute accuracy of the point data shall be 0.5’ in both the horizontal and vertical planes.

# PROJECT SPECIFICATIONS

# Route

{Description of Line Route}.  The approximate length of this line is {length of route}.  The width of coverage shall be a minimum of {100 Note: for existing lines one may wish to consider a much smaller width} feet left and right from the route centerline

Drawing {Drawing Number(s)} dated {mm/dd/yy}, represents the current proposed location of the transmission line.

# Coordinate System

The survey data and all attachments or references shall be in {UTM, State Plane, etc. – full description}. Any PLS-CADD .bak files delivered with data will also have their coordinate system defined with the same coordinate system.

# Survey Method

The survey method should adhere to Section {5.1, 5.2} below for {Traditional Ground, Aerial Lidar} Survey.

# TECHNICAL SPECIFICATIONS

# Feature Code

The Contractor shall use the feature code table provided with this specification for all point classification.  A PLS-CADD .fea file is also available from the prom the project engineer for use in the PLS-CADD .bak file deliverable. See Appendix A for the feature code table.

# Structure Photography

For surveys of existing transmission lines, digital still photographs shall be obtained for each transmission structure.

The structure photographs shall be color digital in the .jp2 or .png format with a minimum resolution of 16 mega-pixels.

Aerial structure photos shall either be at a 45 degree angle or taken from the ground.  The entire structure shall be captured in the photo.

The digital photograph shall be incorporated into the deliverable such that they can be called up at any specific structure location in PLS-CADD.

# Meteorological Data and Weather Stations

When providing data of an existing line or at the discretion of the project engineer, the Contractor shall collect the following meteorological data by use of a helicopter mounted weather probe and/or weather stations to obtain an accurate representation of weather conditions throughout the duration of the survey:

- Date

- Time

- Ambient air temperature (°F)

- Wind speed (ft/s)

- Wind direction (°) – a value of 0 indicates a wind direction towards North, 90 towards East)

- Sky conditions

- Solar radiation (W/ft2)

The Contractor shall monitor and collect weather data such that the engineer can                                use the data to analyze and design their transmission lines. The type and number of weather stations shall be detailed in the Contractor’s work plan and approved by the project engineer.

The Contractor shall space their weather stations no more than 15 miles apart.  In mountainous terrain, the Contractor shall place their weather stations such that each major valley has at least one weather station. This is advisable due to frequent, significant differences in weather conditions on either side of mountain ridges in the project area.  This may require that weather stations be spaced significantly less than 15 miles apart.

Data shall be collected, at a minimum, of every five minutes for LiDAR survey and at every instance of overhead wire data collection for Traditional Ground survey.

The weather stations shall have a minimum accuracy of:

- Ambient air temperature: 0.5°F

- Temperature range: -30°F to 150°F

- Wind threshold speed: 0.3 MPH

- Wind speed accuracy range: 0.3 MPH to 130 MPH

- Wind direction: 10°

# SURVEY METHOD

# Traditional Ground Survey

In addition to the items listed below, the contractor shall provide photographs and field notes for all traditional ground surveys.

# Existing Structures

Existing structures shall have the following features surveyed:

- Top of structure – pole, lattice tower, etc.

- Base of structure – pole, base plate, each lattice tower leg, etc.

- Wire attachment points – point where the wire and the insulator (or clamp) meet

- Insulator attachment points –point where the insulator meets the structure

- Structure attachment points – point where items like crossarms, x-braces, and guys are attached to the structure

# Existing Overhead Wire

All existing shield wires and transmission, distribution, and communication conductors are to be surveyed.  All wires survey should include a minimum of five (5) locations per span, including the mid-span (low-point) of conductors.

All distribution and service taps and crossings are to be surveyed out to the second structure (where possible).  See section 5.1.1 for details on surveying the crossing and tap structures.

Any equipment on the wires shall also be surveyed and photographed, including marker balls, detuning pendulums, and bundle spacers unless project engineer specifies differently.

Contractor shall ensure the information provided in section 4.3 for the meteorological data specifically applies to any crossing wires.

# Existing Terrain and Underground Facilities

All underground facilities shall be located and captured.  The locate flags, with underground facility owners listed, shall be photographed according to the project engineer’s discretion.

The existing terrain shall be surveyed such that a representative ground profile can be determined.  A minimum of one point every 10 feet along the centerline shall be collected.  In addition, the Contractor shall collect one point a minimum of {50 Note: different widths should be considered for different voltages} feet left and right from the route centerline in 10’ increments.  In addition, the Contractor shall differentiate between ground and farm fields, roadways, sidewalks, water bodies, streams, drainage ditches, culverts, top of slope, and toe of slope features as shown in the feature code table.

# Existing Obstructions and Features

All aerial and ground obstructions shall be captured.  This includes, but is not limited to the following:

- Guy Wires

- Anchors

- Equipment

- Buildings – Residential, Commercial, Storage, etc.

  - Enough points shall be surveyed to outline the building

- Roof Peaks - nearest survey centerline

  - Enough points shall be surveyed to outline the roof peak

- Fences

- Streetlights

- Pools

- Playgrounds

- Wells

- Outline of Signs and Billboards

- Irrigation Systems

- Bridges

- Railroad Tracks

- Railroad Appurtenances (e.g. x-ing arms, connection points, lights, etc.)

- LP and Fuel Tanks

- Silos, Grain Bins, Farm Equipment etc.

- Any other additional miscellaneous clearance obstructions

# Aerial LiDAR

The Contractor shall record flight start and stop times for each line, deliver the data in .LAS or .LAZ file format, and show aircraft position and time in a vector file (dxf or shp files).

# Data Acquisition

All LIDAR-derived coordinates shall be three-dimensional with a sufficient density to satisfy the requirements of this specification.  Sufficient density shall also constitute the ability to develop a detailed surface model of the ground surface over the entire width of the surveyed corridor which can be rendered to a TIN in PLS-CADD.  The Contractor shall extract coordinates from all topographical features, above ground obstacles, and features which would impact the design or analysis of transmission lines.  The Contractor shall ensure the accuracy of his work so that extensive ground verification shall not be required.

All LIDAR-derived coordinates shall be referenced using the coordinate system from section 3.2.

All LIDAR-derived coordinates shall be assigned feature codes according to the feature code table found in Appendix A of this document.

All LIDAR-derived feature-coded coordinates shall be interpreted from the LIDAR data and shall not be depicted as ‘point clouds’.  For example, in the case a building, the corner positions shall be calculated and delivered as points.  Acceptance of the ‘closest LIDAR return’ shall not be permitted.

# LiDAR Acquisition:

LiDAR pulse rates, helicopter altitude, and speed shall be established such that:

    - Point Densities shall be a minimum of 15 points per square meter

    - Frequency shall be a minimum of 50 kHz

    - Up to four (4) return values per pulse. No first or last pulse only systems are to be used.

    - Statistics on the data shall be collected, including average point density, frequency, pulse rate, satellite coverage, and meteorological information.  Detailed meteorological specifications are found in the section 4.3 of this document.

# LiDAR Equipment:

The Aerial LIDAR Contractor shall submit a full description of the LIDAR unit to be used, along with certificates of calibration.

The LIDAR system is required to be FDA certified to be eye safe, and shall have an automatic shutdown feature.

The LIDAR system shall be capable of collecting four (4) coordinate points from each laser pulse.

# Ground Control

The Contractor shall provide adequate GPS base stations along the right of way of each transmission line to support the LIDAR data accuracy requirements.  GPS base stations shall not be placed at excessive intervals resulting in gap areas, and shall have at all times adequate overlap between stations.

The Contractor shall provide a Ground Control Report(s) outlining all ground control points used during the survey. Reports shall be generated for each line surveyed.

# Ground Truthing

Contractor(s) shall field-verify LiDAR data by collecting ground truth data along the surveyed corridor on surfaces considered permanent and/or semi-permanent.

A snow tolerance of up to 0’-6” of snow will be acceptable provided that depths are recorded at ground control and ground truthing locations.

Contractor(s) shall use one (1) of the three (3) options below to generate the ground truthing reports:

- Ground truth variance reports that calculate the expected accuracy of the laser-scan by comparing laser points immediately adjacent to known USGS monuments to the absolute location of the USGS monuments that are referenced for the LIDAR capture flights.  At least two accuracy checks will be made for each transmission line; OR

- Ground truth variance reports that calculate the expected accuracy of the laser-scan by comparing laser points immediately adjacent to known USGS survey control monuments to the absolute location of the USGS survey control monuments that are referenced for the LIDAR data capture flights.  The LIDAR accuracy reports will also calculate the achieved accuracy of the laser scan by comparing laser points along permanent or semi-permanent surfaces to actual surveyed points along the same permanent or semi-permanent surfaces.  An accuracy check will be made at least every ten miles along a right-of-way.  At least two accuracy checks will be made for each transmission line; OR

- Ground truth variance reports that calculate and check the achieved accuracy of the laser-scan by comparing, in a selected area, the locations of 20 ground survey points along pavement, 20 ground survey points along a grassy area, 20 ground survey points along a brush area, and 20 ground survey points along a forested area of the transmission line with LIDAR (laser scan) points in the same locations.  An accuracy check will be made at least every 10 miles along a right-of-way.  At least two accuracy checks will be made for each transmission line.

The ground truth variance report will include the following:

- Average statistical deviations of vertical data.

- Minimum and maximum statistical deviation of vertical data.

- Statistical verification of confidence levels.

# Aerial Imagery

Digital, color, full motion, forward looking 45 degree video shall be acquired.  The video shall cover the whole corridor width, shall be delivered in MPEG format, and shall be fully integrated with PLS-CADD.

The Contractor shall provide full color georeferenced, ortho-rectified aerial photography for the entire width and length of the transmission corridor.  The Contractor shall acquire the imagery at the highest sun-angle possible, limiting shadows.

The Contractor shall provide the photographs in the either .jp2 or .png format with no image collars and incorporate them into the PLS-CADD deliverable.

# DELIVERABLES

# Specific Deliverables

The following deliverables will be provided:

- All projects shall be delivered in the coordinate system delineated in section 3.2 of this specification.

- All project notes and structure photography shall be included in a .zip file.

- Meteorological report and weather data shall be included in a .zip file.

- For LiDAR surveys, the Ground Truthing Report, Survey Control Report, and Video file shall be included.

- Either the Traditional Ground Survey data file as described in section 6.2 or the PLS-CADD design as described in section 6.3.

# Traditional Ground Survey Data File

All Traditional Ground Survey will be provided in one of the following formats:

- .csv (comma separated value)

- .xlsx (Excel spreadsheet)

- .asc (ASCII text)

- .txt (text – no formatting, space separated)

- .dxf (drawing interchange format) – ASCII based, not binary

# PLS-CADD Design File

For all Aerial LiDAR surveys, a PLS-CADD design file will be the main deliverable for the Contractor.  Each design file shall include the following:

- PLS-CADD .BAK file containing the feature coded XYZ data as found in Appendix A.

- LiDAR Data in .las or .laz format. LiDAR Data shall be organized so all associated survey data loaded into the individual PLS-CADD.BAK files is contained within a folder with the same name.

  - Vegetation XYZ data shall be provided in a separate .las or .laz files that contain all vegetation for each individual PLS-CADD .BAK file.

- Digital, color, georeferenced, ortho-rectified photography in either .jp2 or .png format

- Digital video of the corridor in MPEG format

- Planimetric drawing of the corridor in ASCII DXF format (not binary).  The drawing shall be for the entire width and length of the corridor and shall be in one complete file.  The drawing shall include, but is not limited to:

  - Transmission centerline of the circuit being surveyed

  - State plane coordinates and deflection of each PI

  - Streets, roads, and highway centerlines and edge of pavement

  - Edge of unpaved roads, trails, and driveways

  - Centerlines and base of poles for any utilities within the survey corridor

  - Fences

  - All structures, including homes, sheds, garages, barns, buildings, windmills, antennas.  The outline or footprint of each of these features shall be depicted

  - Banks and centerlines of creeks, streams, rivers, ponds, and lakes

  - Areas of forestation.  Drip edges for trees and groups of trees and brush shall be shown

# APPENDIX A

A list of codes required to define the characteristic feature of surveyed points is as follows.  Feature codes shall be consistent for each point type or discreet feature.  Alternate points, shall be approved by Engineer prior to commencement of the survey work.

FEATURE CODES

| Feat. Code | Feature Description |
| --- | --- |
| 1 | PI |
| 2 | INTERPOLATED POINTS |
| 10 | GROUND |
| 11 | GROUND - PEDESTRIAN ONLY |
| 12 | GROUND - CENTER PROFILE |
| 13 | GROUND - LEFT PROFILE |
| 14 | GROUND - RIGHT PROFILE |
| 20 | AGRICULTURE - ACTIVE |
| 21 | AGRICULTURE - INAVTIVE |
| 22 | FIELD - EDGE OF |
| 23 | FIELD ROAD |
| 30 | ROAD - EDGE OF |
| 31 | ROAD - PAVED |
| 32 | ROAD - UNPAVED |
| 33 | ROAD - CENTERLINE |
| 35 | PARKING |
| 36 | PARKING - EDGE OF |
| 40 | DRIVEWAY - RESIDENTIAL |
| 41 | DRIVEWAY - COMMERCIAL |
| 42 | DRIVEWAY - EDGE OF |
| 43 | DITCH |
| 44 | DITCH - CENTERLINE |
| 45 | DRAIN |
| 46 | DRAIN - CENTERLINE |
| 47 | CULVERT |
| 60 | FENCE - BASE |
| 61 | CURB |
| 62 | SIDEWALK |
| 63 | PAVEMENT |
| 70 | CAMPGROUND |
| 71 | CEMETERY - EDGE OF |
| 72 | TRAIL - EDGE OF |
| 73 | TREE LINE - EDGE OF |
| Feat. Code | Feature Description |
| 74 | LAND FILL - EDGE OF |
| 75 | QUARRY - EDGE OF |
| 76 | PROPERTY - CORNER |
| 77 | PROPERTY - LINE |
| 78 | PLAYGROUND - EDGE OF |
| 90 | RAILROAD - CL |
| 91 | RAILROAD - CROSSING |
| 92 | RAILROAD - RAILS |
| 100 | WATER (UNDETERMINED) |
| 101 | WATER - EDGE OF |
| 102 | WATER - HIGH WATER LINE |
| 103 | CREEK - EDGE OF |
| 104 | CREEK - CENTERLINE |
| 105 | CREEK - HIGH WATER LINE |
| 106 | CREEK - DRY CREEK BED |
| 107 | WETLAND - EDGE OF |
| 110 | WATER - NOT SUITABLE FOR SAILBOATING |
| 111 | WATER (NO RAMP) - LESS THAN 20 ACRES |
| 112 | WATER (NO RAMP) - 20 - 200 ACRES |
| 113 | WATER (NO RAMP) - 200 - 2000 ACRES |
| 114 | WATER (NO RAMP) - OVER 2000 ACRES |
| 121 | WATER (WITH RAMP) - LESS THAN 20 ACRES |
| 122 | WATER (WITH RAMP) - 20 - 200 ACRES |
| 123 | WATER (WITH RAMP) - 200 - 2000 ACRES |
| 124 | WATER (WITH RAMP) - OVER 2000 ACRES |
| 200 | POLE - BASE |
| 210 | H-FRAME - CL |
| 211 | H-FRAME - POLE BASE |
| 220 | LATTICE - CL |
| 221 | LATTICE - LEG BASE |
| 230 | TOWER - CL |
| 231 | TOWER - LEG CL |
| 240 | ANCHOR |
| 300 | GAS - METER |
| 301 | GAS - VALVE |
| 302 | GAS - WELL |
| 310 | WATER - METER |
| 311 | WATER - VALVE |
| 312 | WATER - WELL |
| 320 | BUILDING (AT GND) |
| Feat. Code | Feature Description |
| 325 | HOUSE (AT GND) |
| 330 | SCHOOL (AT GND) |
| 340 | MANHOLE |
| 341 | MANHOLE - ELECTRIC |
| 342 | MANHOLE - GAS |
| 343 | MANHOLE - TELEPHONE |
| 344 | MANHOLE - STORM AND SEWER |
| 350 | UNDERGROUND - ELECTRIC |
| 351 | UNDERGROUND - UTILITY |
| 352 | UNDERGROUND - TELEPHONE |
| 353 | UNDERGROUND - GAS |
| 354 | UNDERGROUND - WATER |
| 500 | ANTENNA |
| 505 | BILLBOARD |
| 510 | BRIDGE - DECK |
| 511 | BRIDGE - GUARD RAILING - TOP |
| 512 | BRIDGE - RAILROAD - EDGE OF |
| 513 | BRIDGE - WALKING - BICYCLE |
| 514 | BRIDGE - WITH SUPERSTRUCTURE |
| 515 | BRIDGE - WITHOUT SUPERSTRUCTURE |
| 520 | BUILDING |
| 521 | BUILDING - TOP |
| 530 | CONVEYOR SYSTEM |
| 535 | DIVING PLATFORM |
| 540 | FENCE - CORNER |
| 541 | FENCE - POST |
| 542 | FENCE - SUBSTATION |
| 543 | FENCE - TOP |
| 545 | FIRE HYDRANT |
| 550 | FLAG POLE |
| 555 | GATE |
| 560 | GRAIN BIN - W/PERMANENT EQUIP |
| 565 | GRAIN BIN - W/PORTABLE EQUIP |
| 570 | IRRIGATION - TOP |
| 575 | MAST |
| 576 | MISC STR OR OBJECT |
| 580 | OVERHEAD WALKWAY |
| 581 | PHONE BOOTH |
| 585 | PIPELINE - ABOVE GROUND |
| 590 | ROOF (ACCESSIBLE) |
| Feat. Code | Feature Description |
| 591 | ROOF (NOT ACCESSIBLE) |
| 600 | RR - COMMUNICATION LINE |
| 601 | RR - SIGNAL - TOP |
| 602 | RR - SIGNAL LIGHT-BARRIER - TOP |
| 610 | SIGN (W/OUT PEDESTRIAN ACCESS) - TOP |
| 611 | SIGN (W/PEDESTRIAN ACCESS) - TOP |
| 615 | SOLAR PANEL |
| 620 | STREETLIGHT - TOP |
| 625 | SWIMMING POOL |
| 630 | TANK |
| 631 | TANK - TOP |
| 635 | TRAFFICE SIGNAL TOP |
| 640 | TREE |
| 641 | TREE - STUMP |
| 642 | TREE - TOP |
| 645 | VEGETATION |
| 650 | WALL |
| 655 | WELL |
| 1000 | CROSSING - DISTRIBUTION |
| 1005 | CROSSING - 69KV |
| 1010 | CROSSING - 115KV |
| 1015 | CROSSING - 138KV |
| 1020 | CROSSING - 230KV |
| 1025 | CROSSING - 345KV |
| 1080 | CROSSING - SHIELD WIRE |
| 1085 | CROSSING - UNIDENTIFIED |
| 1200 | WIRE - UNIDENTIFIED |
| 1205 | WIRE - SERVICE DROP |
| 1210 | WIRE - SHIELD WIRE |
| 1211 | WIRE - FIBER OPTIC |
| 1215 | WIRE - TELEPHONE |
| 1220 | WIRE - DISTRIBUTION |
| 1225 | WIRE - 69KV |
| 1230 | WIRE - 115KV |
| 1235 | WIRE - 138KV |
| 1240 | WIRE - 230KV |
| 1245 | WIRE - 345KV |
| 1250 | WIRE - 500KV |
| 1500 | GUY WIRE |
| 1501 | GUY WIRE - CATV |
| Feat. Code | Feature Description |
| 1502 | GUY WIRE - DISTRIBUTION |
| 1503 | GUY WIRE - EXISTING |
| 1504 | GUY WIRE - TELEPHONE |
| 1505 | GUY WIRE - TRANSMISSION |
| 1510 | JUMPERS |
| 1515 | POLE - DISTRIBUTION TOP |
| 1516 | POLE - STREETLIGHT TOP |
| 1517 | POLE - TRANSMISSION TOP |
| 1518 | POLE - UNIDENTIFIED TOP |
| 1520 | STRUCTURE |
| 1521 | STRUCTURE - ARM |
| 1522 | STRUCTURE - BRACE |
| 1523 | STRUCTURE - EXISTING |
| 1524 | STRUCTURE - FOUNDATION |
| 1525 | STRUCTURE - H-FRAME |
| 1526 | STRUCTURE - SUBSTATION |
| 1530 | TOWER - CL TOP |
| 1531 | TOWER - MICROWAVE |
| 1532 | TOWER - OBSERVATION |
| 1533 | TOWER - TL |
| 1534 | TOWER (GUYED) - LATTICE TOP |
| 1550 | CABLE ATT - TELEPHONE |
| 1551 | CABLE ATT - FIBER OPTIC |
| 1552 | CABLE ATT - SERVICE DROP |
| 1560 | SW ATT 1A |
| 1561 | SW ATT 1B |
| 1562 | SW ATT 2A |
| 1563 | SW ATT 2B |
| 1564 | SW ATT 3A |
| 1565 | SW ATT 3B |
| 1566 | SW ATT 4A |
| 1567 | SW ATT 4B |
| 1580 | INS ATT 1A |
| 1581 | INS ATT 1B |
| 1582 | INS ATT 1C |
| 1583 | INS ATT 2A |
| 1584 | INS ATT 2B |
| 1585 | INS ATT 2C |
| 1586 | INS ATT 3A |
| 1587 | INS ATT 3B |
| Feat. Code | Feature Description |
| 1588 | INS ATT 3C |
| 1589 | INS ATT 4A |
| 1590 | INS ATT 4B |
| 1591 | INS ATT 4C |
| 1600 | INSULATOR 1A |
| 1601 | INSULATOR 1B |
| 1602 | INSULATOR 1C |
| 1603 | INSULATOR 2A |
| 1604 | INSULATOR 2B |
| 1605 | INSULATOR 2C |
| 1606 | INSULATOR 3A |
| 1607 | INSULATOR 3B |
| 1608 | INSULATOR 3C |
| 1609 | INSULATOR 4A |
| 1610 | INSULATOR 4B |
| 1611 | INSULATOR 4C |
| 1620 | SW 1A |
| 1621 | SW 1B |
| 1622 | SW 2A |
| 1623 | SW 2B |
| 1624 | SW 3A |
| 1625 | SW 3B |
| 1626 | SW 4A |
| 1627 | SW 4B |
| 1640 | COND 1A |
| 1641 | COND 1B |
| 1642 | COND 1C |
| 1643 | COND 2A |
| 1644 | COND 2B |
| 1645 | COND 2C |
| 1646 | COND 3A |
| 1647 | COND 3B |
| 1648 | COND 3C |
| 1649 | COND 4A |
| 1650 | COND 4B |
| 1651 | COND 4C |
| 1660 | DIST 1A |
| 1661 | DIST 1B |
| 1662 | DIST 1C |
| 1663 | DIST 2A |
| Feat. Code | Feature Description |
| 1664 | DIST 2B |
| 1665 | DIST 2C |
| 1670 | NEUTRAL |
| 1675 | COMM 1 |
| 1676 | COMM 2 |
| 1677 | COMM 3 |
| 2200 | ?UNKNOWN FEATURE CODE? |

*Note:	Assign other feature codes for other miscellaneous features, as necessary.  The same feature code shall be used for each type of feature, and consistency shall be maintained in grouping the new feature code near similar codes of other features.  The use of miscellaneous features shall be kept to a minimum, and additional feature codes added shall be provided to the Engineer.