## Slide 1: IT 4823 Information Security Administration
Power Management

## Slide 2: Power Management
Electrical quantity (voltage level; amperage rating) is a concern, as is quality of power (cleanliness; proper installation)
Noise that interferes with the normal 60 Hertz cycle can result in inaccurate time clocks
Overloading a circuit causes problems with circuit tripping and can overload electric conductors, increasing risk of fire if breakers are not properly sized.

## Slide 3: Grounding
“Neutral” conductor: carries the return current of a circuit. Bonded to the center tap of a transformer.
Safety ground: often also bonded to the center tap of the transformer; should be connected to earth ground.
Signal ground or reference ground: a reference for low-voltage signals.

## Slide 4: Power Circuits
American Power Conversion

## Slide 5: Typical Wiring
American Power Conversion

## Slide 6: Reversed Plug or Wiring
American Power Conversion
Equipment on/off switch disconnects neutral, not hot. The load is still connected to the hot leg of the circuit.

## Slide 7: Why Three Wires?
American Power Conversion

## Slide 8: Purpose of Safety Ground
American Power Conversion
A fault in the load opens the circuit breaker because current flows through the safety ground.

## Slide 9: Without Safety Ground !
American Power Conversion

## Slide 10: Dedicated Circuits
Purpose: to isolate computer equipment from other loads
Other loads can trip circuit breakers!
Some loads (large motors, fluorescent lights) generate electrical noise

## Slide 11: Determining Power Requirements
Watts: power consumed; heat dissipated
Volt-amps: apparent power; voltage times current.
W = PF * VA
  For power-factor-corrected power supplies, W=VA (PF = 1)
  For “small” equipment, PF is about 0.60, and W will be less than VA.
UPSs have both a maximum Watt rating and a maximum VA rating

## Slide 12: Determining Power Requirements
HVAC
Lighting
“Convenience” power
These may be interrupted briefly.

## Slide 13: Uninterruptible Power Supply (UPS)
In case of power outage, UPS is backup power source for major computer systems
Four basic UPS configurations:
  Standby
  Line-interactive
  True online (double conversion online)
  Rotating (motor-generators)
  Also, ferroresonant transformer UPSs for industrial use.

## Slide 14: UPS Sizes
To 1,000 VA:
1 to 2.5 kVA:
2.5 to 10 kVA:
10 to 100 kVA:
100 + kVA:
Desktop equipment Servers, etc.
Small computer rooms Data centers
Large installations

## Slide 15: Runtime of UPS Systems
Generally measured in minutes.
Important factors in run time:
  Percent of full load
  Battery capacity.
Batteries have a limited lifetime: 3 – 7 years.
The UPS is out of service while batteries are being replaced.

## Slide 16: UPS Output Waveforms
Alternating current delivered by power utilities is a 60 Hz sine wave.
UPSs can also produce sine wave power…
But not all of them do. It is cheaper to make a UPS that generates a “stepped square wave” that supposedly approximates the sine wave.

## Slide 17: Sine Wave from Utility Power
Oscillogram by Warrren Young, Creative Commons BY-SA License http://superuser.com/questions/912679/when-do-i-need-a-pure-sine-wave-ups

## Slide 18: From a “True Sine Wave” UPS
Oscillogram by Warrren Young, Creative Commons BY-SA License http://superuser.com/questions/912679/when-do-i-need-a-pure-sine-wave-ups

## Slide 19: From a “Stepped Square Wave” UPS
Oscillogram by Warrren Young, Creative Commons BY-SA License http://superuser.com/questions/912679/when-do-i-need-a-pure-sine-wave-ups

## Slide 20: Do I Need a Sine Wave?
For computer equipment, possibly not; a good computer power supply should be able to deal with ugly power.
For audio or video equipment, and equipment with active power factor correction, yes.
UPSs last forever; over dozen years, the major cost will be battery replacement, not initial price.
Conclusion: Buy the more expensive model with sine wave output.

## Slide 21: “Smart” UPSs
Many UPSs have built-in monitoring
  Voltage
  Current
  Failures
  Battery state
Small and medium UPSs are available with a USB connection to communicate with a server.
Software is available to shut down a server before UPS battery is exhausted.

## Slide 22: Emergency and Standby Generators
Emergency generators
  Legally required in many cases.
  For life-safety equipment.
  Power available within ten seconds.
  Require separate power distribution routing.
Standby generators
  May or may not be legally required
  Power equipment not related to life safety.
  Power available within 60 seconds.

## Slide 23: Continuous and Prime Power Generators
Continuous power generators: Provide power to a load with limited fluctuation for years at a time.
Prime power generators: Provide power to a fluctuating load for years at a time.
Reciprocating engines or gas turbines.
Unusual in the data center environment.

## Slide 24: Fueling Generators
Gasoline: Not practical for emergency or standby applications; dangerous; fuel has limited lifetime.
Diesel: Run time is limited to storage tank size; refueling may not be possible in some kinds of emergencies.
Propane: Same considerations as Diesel.
Natural gas: Potentially unlimited run time, but depends on natural gas utility.

## Slide 25: Designing Power Systems
Transfer Switch
Utility Power
Generator
Transfer Switch
Non- Critical Load
Critical Load
UPS
Maintenance Bypass

## Slide 26: Dual-Corded Systems
Power Supply
Power Supply
For most effective use, the power to each power supply should be independent, i.e. two UPSs on different circuits.
One
Socket?
Expensive Server

## Slide 27: Emergency Shutoff
An important aspect of power management is the need to be able to stop power immediately should current represent a risk to human or machine safety
Most computer rooms and wiring closets equipped with an emergency power shutoff
Accident-resistant cover is essential

## Slide 28: Energy Management
Energy is a significant cost in medium and large data centers.
Cooling is a substantial portion of that cost.
Energy management can significantly lower costs.

## Slide 29: Demand Billing and Load Shedding
Utility companies offer “demand rate” billing to medium and large customers.
The rate per kilowatt-hour varies hourly with the demand on the utility’s generating resources.
Businesses that can reduce load during times of peak demand can realize significant savings.

## Slide 30: Load Shedding Strategies
Local generation: Use locally generated power for HVAC during peak periods.
Store pre-chilled water for cooling use during peak periods.
“Spin down” some disks during peak periods, or always.
Reduce clock speed, shut down idle cores in servers not under load.
Relocate workloads to “the cloud.”

## Slide 31: Alternative Power Sources
Use 208 or 420 V. power distribution to reduce losses due to step-down conversions.
Use DC power distribution. (Probably suitable only for completely new data centers. See the Open Compute Project.)
Consider solar panels.
Consider fuel cell generators rather than Diesel or natural gas internal combustion generators.
Check economics of continuous generation.

## Slide 32: DCIM Software
“Data Center Infrastructure Management”
Energy monitoring
Ability to power down idle servers.
Collects data for capacity planning.

## Slide 33: Questions